## Sheet1
No. | Name | Type | Description | BIS Standards | Unit
1 | FIT-101 | Sensor | Flow meter; Measures inflow into raw water tank. | 5 | m3/h
2 | LIT-101 | Sensor | Level Transmitter; Raw water tank level. | 0 to 1000 | L
3 | MV-101 | Actuator | Motorized valve; Controls water flow to the raw water tank. | 0,1,2
4 | P-101 | Actuator | Pump; Pumps water from raw water tank to second stage. | 1 or 2
5 | P-102 (backup) | Actuator | Pump; Pumps water from raw water tank to second stage. | 1 or 2
6 | AIT-201 | Sensor | Conductivity analyser; Measures NaCl level. | 200 to 800 max till 2000 admissible | mg/L
7 | AIT-202 | Sensor | pH analyser; Measures HCl level. | 6.5-8.5
8 | AIT-203 | Sensor | ORP analyser; Measures NaOCl level. | 200 to 650 if closer to 200 high alarm 600-650 desirable | mV
9 | FIT-201 | Sensor | Flow Transmitter; Control dosing pumps. | 5 | m3/h
10 | MV-201 | Actuator | Motorized valve; Controls water flow to the UF feed water tank. | 0,1,2
11 | P-201 | Actuator | Dosing pump; NaCl dosing pump. | 1 or 2
12 | P-202 (backup) | Actuator | Dosing pump; NaCl dosing pump. | 1 or 2
13 | P-203 | Actuator | Dosing pump; HCl dosing pump. | 1 or 2
14 | P-204 (backup) | Actuator | Dosing pump; HCl dosing pump. | 1 or 2
15 | P-205 | Actuator | Dosing pump; NaOCl dosing pump. | 1 or 2
16 | P-206 (backup) | Actuator | Dosing pump; NaOCl dosing pump. | 1 or 2
17 | DPIT-301 | Sensor | Differential pressure indicating transmitter; Controls the back-wash process. | 4 to 20 | mA
18 | FIT-301 | Sensor | Flow meter; Measures the flow of water in the UF stage. | 5 | m3/h
19 | LIT-301 | Sensor | Level Transmitter; UF feed water tank level. | 0 to 1000 | L
20 | MV-301 | Actuator | Motorized Valve; Controls UF-Backwash process. | 0,1,2
21 | MV-302 | Actuator | Motorized Valve; Controls water from UF process to De- Chlorination unit. | 0,1,2
22 | MV-303 | Actuator | Motorized Valve; Controls UF-Backwash drain. | 0,1,2
23 | MV-304 | Actuator | Motorized Valve; Controls UF drain. | 0,1,2
24 | P-301 (backup) | Actuator | UF feed Pump; Pumps water from UF feed water tank to RO feed water tank via UF filtration. | 1 or 2
25 | P-302 | Actuator | UF feed Pump; Pumps water from UF feed water tank to RO feed water tank via UF filtration. | 1 or 2
26 | AIT-401 | Sensor | RO hardness meter of water. | Near 200 worst case 600 tak | mg/L
27 | AIT-402 | Sensor | ORP meter; Controls the NaHSO3dosing(P203), NaOCl dosing (P205). | <250 high alaram at 250 | mV
28 | FIT-401 | Sensor | Flow Transmitter ; Controls the UV dechlorinator. | 0.2–1.0 | mg/L
29 | LIT-401 | Actuator | Level Transmitter; RO feed water tank level. | 0 to 1000 | L
30 | P-401 (backup) | Actuator | Pump; Pumps water from RO feed tank to UV dechlorinator. | 1 or 2
31 | P-402 | Actuator | Pump; Pumps water from RO feed tank to UV dechlorinator. | 1 or 2
32 | P-403 | Actuator | Sodium bi-sulphate pump. | 1 or 2
33 | P-404 (backup) | Actuator | Sodium bi-sulphate pump. | 1 or 2
34 | UV-401 | Actuator | Dechlorinator; Removes chlorine from water. | 1 or 2
35 | AIT-501 | Sensor | RO pH analyser; Measures HCl level. | 6.5 to 8.5
36 | AIT-502 | Sensor | RO feed ORP analyser; Measures NaOCl level. | 200 to 650 if closer to 200 high alarm 600-650 desirable | mV
37 | AIT-503 | Sensor | RO feed conductivity analyser; Measures NaCl level. | 200 to 800 max till 2000 admissible | mg/L
38 | AIT-504 | Sensor | RO permeate conductivity analyser; Measures NaCl level. | 200 to 800 max till 2000 admissible | mg/L
39 | FIT-501 | Sensor | Flow meter; RO membrane inlet flow meter. | 8.0 – 9.0 | m3/h
40 | FIT-502 | Sensor | Flow meter; RO Permeate flow meter. | 0 – 6.0 | m3/h
41 | FIT-503 | Sensor | Flow meter; RO Reject flow meter. | 3.0 – 4.0 | m3/h
42 | FIT-504 | Sensor | Flow meter; RO re-circulation flow meter. | 6.0 – 8.0 | m3/h
43 | P-501 | Actuator | Pump; Pumps dechlorinated water to RO. | 1 or 2
44 | P-502 (backup) | Actuator | Pump; Pumps dechlorinated water to RO. | 1 or 2
45 | PIT-501 | Sensor | Pressure meter; RO feed pressure. | 2 to 4 <2 not allowed keep in 2. to 3.5 range | bar
46 | PIT-502 | Sensor | Pressure meter; RO permeate pressure. | >1 is not admissible keep between 0.3 to 0.5 | bar
47 | PIT-503 | Sensor | Pressure meter;RO reject pressure. | 1.5 to 2.5 bar if =feed pressure attack possible
48 | FIT-601 | Sensor | Flow meter; UF Backwash flow meter. | 24 to 36 | m3/h
49 | P-601 | Actuator | Pump; Pumps water from RO permeate tank to raw water tank (not used for data collection). | 1 or 2
50 | P-602 | Actuator | Pump; Pumps water from UF back wash tank to UF filter to clean the membrane. | 1 or 2
51 | P-603 | Actuator | Not implemented in SWaT yet. | 1 or 2